TIPS:

Editor's Notes to the specifier are in hidden text in highlighted boxes as Word Style CMT. These may be deleted from final copy if desired by searching for Style CMT in the "Find What" dialog and leaving "Replace With" empty.

To view non-printing Editor's Notes that provide guidance for editing, do the following:
Word 2003 - On the Tools menu, click Options, and then click the View tab. Under Formatting marks, select Hidden Text
Word 2007 - Click the Microsoft Office Button, and then click Word Options. Click Display. Under Always show these formatting marks on the screen, select Hidden Text
Word 365 - Click File Options Display, and then under Always show these formatting marks on the screen, select Hidden Text

Notice: The information in this specification is subject to change without notice. CGC Inc. or USG Corp. assumes no responsibility for any errors that may inadvertently appear in this specification.

GENERAL NOTES TO SPECIFIER:

This Specification Section has been prepared to assist design professionals in the preparation of project or office master Specifications. It follows guidelines established by the Construction Specifications Institute (CSI), and therefore may be used with most master Specification systems with minor editing.

Electronic versions of this specification utilize automatic paragraph numbering based on Microsoft Word style formatting. To adjust levels of paragraphs assign appropriate style and numbering will automatically adjust.

Edit this specification carefully by deleting and inserting text to suit Project-specific requirements. Modify as necessary and delete items that are not applicable. Verify that referenced Section titles are correct. (Titles and Section Numbers referenced are based on CSI MasterFormat, 2020 edition).

This is written as a closed proprietary specification. At the time of preparation no other System Vendors were known to have a comparable system. Review and modify to suit Project requirements and specifiers' practice. Optional items requiring selection by the specifier are enclosed within brackets, e.g. [35] [40] [45]. Make appropriate selections and delete others including the brackets themselves. Items requiring additional information are enclosed within brackets with single Guillemots, e.g. [<insert option here>]. Revise header and footer to suit project/office requirements.

When editing is complete, delete all text on this page, then remove the section break at the top of the next page to remove this page from the document.

This Section assumes the Project Manual will contain complete Division 01 documents. Close coordination with Division 01 Sections is required. If the Project Manual does not contain the following sections, additional information should be included under the appropriate articles.

Section 01 25 00 - Substitution Procedures (if substitutions are to be allowed)
Section 01 33 00 - Submittal Procedures
Section 01 62 00 - Product Options
Section 01 66 00 - Product Storage and Handling Requirements
Section 01 74 00 - Cleaning And Waste Management
Section 01 77 00 - Closeout Procedures
Section 01 78 00 - Closeout Submittals

This section is copyrighted by USG Corporation. (December, 2022). For additional information contact 
USG Corporation
550 West Adams Street
Chicago, IL 60661
Customer Service: 800-950-3839 / Product Technical Support: 800-874-4968
https://www.usg.com/

| Release No. | Release Date | Release Title "Released for…." | Description of Development / Changes |
| --- | --- | --- | --- |
| Ver 1A | Dec 7, 2022 | First pass - GLOW | Modify from BARZ to GLOW |
| Ver 2A | Dec 13, 2022 | Second pass | Incorporate JAH revisions |

SECTION 09 58 00 - INTEGRATED CEILING ASSEMBLIES

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

LED tape lights integrated into this suspended linear metal ceiling are intended to be decorative and in addition to functional ambient room lighting.

Section includes suspended acoustical metal pan ceiling system with integrated linear LED decorative luminaires and suspension system.

Related Requirements:

Division 21 Sections for fire suppression penetrations through ceiling.

Division 23 Sections for HVAC penetrations through ceiling.

Division 26 Sections for electrical service rough-ins, conduit, devices, wiring, low-voltage wiring work, and connections to electrical power system.

Retain subparagraph above as a general reference to electrical Sections in Division 26 or delete above and list specific Section titles for the appropriate lighting and driver related Sections.

ADMINISTRATIVE REQUIREMENTS

Retain "Preinstallation Meetings" Paragraph below if Work of this Section is extensive or complex enough to justify a meeting.

Preinstallation Meetings: Conduct at [Project site] [<Insert location>].

Coordination: Coordinate with fire suppression, HVAC, electrical, and other work as required to accommodate those systems and prevent interferences with required clearances.

ACTION SUBMITTALS

Product Data: For each type of product. Include driver and dimming protocol.

Shop Drawings: Include the following:

Layout and attachment details.

Locations and details of items which penetrate, are to be coordinated with, or supported by the ceilings.

Ceiling perimeter detail.

Diagrams for power and control wiring including points of connection.

Samples: For each exposed product and for each color and finish specified.

[* * * * * OR * * * * *]

Retain above for single-stage samples. Retain two paragraphs below for two-stage samples.

Samples for Initial Selection: For each type of exposed finish.

Samples for Verification: For each type of exposed finish[ and the following products:]

Sample Sizes: [Manufacturer's standard.] [12 inches long.] [<insert as required>]

Metal pans.

[Exposed edge and opening trim members.]

[Each suspension component.]

Acoustical fill material.

[<Insert list of other samples desired>].

INFORMATIONAL SUBMITTALS

Product Certificates: Manufacturer's certifications that integrated ceiling assembly complies with specified requirements.

Submit certification from the luminaire, driver, or dimmer switch manufacturer that ensures compatibility and operability between devices without flickering and to specified dimming levels.

Coordination Drawings: Plans and other details drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

Details of penetrations through ceiling including:

Lighting fixtures.

Air outlets and inlets.

[Speakers.]

Sprinklers.

Access panels.

Requirements in paragraph below are for test reports for products on which tests are performed either by independent testing agencies or by manufacturers in their own labs. Retain first option if testing is likely to be performed in manufacturer's facilities and witnessed by a qualified testing agency; retain second option if testing is performed by the testing agency.

Product Test Reports: For integrated ceiling assembly, for [acoustic performance] [, FDA,] [and] [fire-resistance] tests performed by [manufacturer and witnessed by a qualified testing agency] [a qualified testing agency].

QUALITY ASSURANCE

Installer Qualifications: Minimum [5] years experience[ under current organizational structure].

DELIVERY, STORAGE, AND HANDLING

Deliver integrated ceiling assembly components to project site in original, unopened packages and store them in a fully enclosed space where they will be protected against damage from moisture, direct sunlight, surface contamination, and other causes.

Handle integrated ceiling assembly components carefully to avoid damage.

FIELD CONDITIONS

Do not install integrated ceiling assemblies until spaces are enclosed and weathertight, wet work in spaces is complete and dry, and work above ceilings is complete.

WARRANTY

[Manufacturer's] [Standard] [Special] Ceiling System Warranty: [Manufacturer agrees] [Manufacturer and Installer agree] to repair or replace components of integrated ceiling assemblies that fail in materials or workmanship within specified warranty period. Failures include, but are not limited to, the following:

Rusting or corrosion.

Excessive sagging or deflection.

Warranty Period: One year from date of Substantial Completion.

[Manufacturer's] [Standard] [Special] Lighting System Warranty: [Manufacturer agrees] [Manufacturer and Installer agree] to repair or replace components of LED luminaires that fail in materials or workmanship within specified warranty period.

Warranty shall include:

All LED drivers and integral control equipment.

Replacement when more than 15 percent of LED sources in any light or light assembly are defective, non-starting, or operating below 70 percent of specified lumen output.

[Replacement when more than 15 percent of LED sources in any light or light assembly show a color shift greater than 0.006 delta u'v' from the zero hour measurement stated in the ANSI/IES LM-79 Test Report.]

Failures include, but are not limited to, the following:

Finish failure or substantial deterioration such as blistering, cracking, peeling, chalking, or fading.

IP20 fixtures carry a 5 year limited warranty. IP65/67/68 fixtures carry a 3 year limited warranty.

LED Luminaire Warranty Period: [3] [5] years from date of Substantial Completion.

PRODUCTS

MANUFACTURERS

Basis-of-Design Product: Subject to compliance with requirements, provide GLOW™ DIRECT WHT ILLUSIONS® by USG® Ceilings Plus®.

Substitutions [will] [will not] be considered.

Single-Source Responsibility: Provide integrated ceiling assemblies and suspension components through one source from a single manufacturer[, unless otherwise acceptable to Architect].

PERFORMANCE CRITERIA

Suspension system is ICC approved in accordance with International Building Code standards for seismic categories A,B,C,D,E,F. Calculations to support slotted grid and “heavy duty” rating available from USG upon request.

The seismic design category (A, B, C, D, E, or F) must be specified on the project drawings by a professional engineer or registered architect per ASCE 7.

IBC allows two paths to determine Seismic Design Category - IBC Section 1613 or ASCE 7 Section 11.6.

Seismic Performance: Comply with [IBC Section 1613] [ASCE/SEI 7 Section 11.6].

Surface-Burning Characteristics: ASTM E84; Class A. Identify products with appropriate markings of applicable testing agency.

Acoustical Performance Requirements: Provide integrated ceiling assemblies without acoustical NRC properties as units are noise reflective.

Regulatory Requirements:

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

INTEGRATED CEILING ASSEMBLY DESCRIPTION

Integrated ceiling assemblies consist of a lay-in, downward accessible, back-lit, metal pan ceiling system comprised of aluminum perforated panels factory-finished for suspending from a direct-hung ceiling suspension system with a panel of LED luminaire modules secured to and supported above the suspension grid.

COMPONENTS

Perforated Metal Panels: Factory-formed units consisting of aluminum panels with minimum 1-1/4 inch integral return edges formed for suspending from 24 by 48 inch ceiling grid system with spring steel clips factory machine riveted to and flush with the return edges of the panels.

Perforation Pattern: [Fractals.] [Waves.] [Tide.] [Flow.] [Pyramids.] [As selected by Architect from manufacturer's full range.]

Finish: Factory applied in the following finish and color:

Saranté® Finish is a faux wood veneer on metal.

Saranté® Finish: [Oak Line.] [Euro Cherry.] [Dark Jatoba.] [Color as selected by Architect from manufacturer's full range.] [<insert color as required>]

[* * * * * OR * * * * *]

Retain above for faux wood finish. Retain below for painted finish.

Painted Finish: Manufacturer's standard paint finish; [Silver Satin] [Blanco Mat®] [Matte Black] [custom] color.

LED Panels: One 14-module LED boards secured to two U-shaped support arms set above the panels with lower ends factory pre-punched for attachment to vertical legs of suspension grid system.

Integrated LUMINAIRES

Provide design information including delivered lumen output, L70 lumen maintenance data, and luminaire efficacy in the luminaire schedule on Project Drawings.

Provide complete system with LED drivers and light sources clearly marked for operation of specific light sources and LED drivers.

Integrated Back Lighting Panel System: GLOW DIRECT WHITE - Illusions by USG Ceilings Plus.

Include required components for backlighting perforated panels including T-Bar LED Module and wiring.

Power Supply: 24v PURE DC Universal Power Supply; Class II Driver [DMX][96W] [96Wx2].

LED module shall be in [3500K] [4000K] [tunable white] [RGBW].

CRI (Color Rendering Index): [90] [95]

Rated Watts/sq-ft: 10.5

Lumen output: [150] [175] [185] [200] [220] [300] [350] lumens per panel

          - Lumen depreciation after 36,000 hours: >90 percent

Controls: tunable white and RGBW systems capable of being controlled by DMX.LED driver and light source package, array, or module shall be accessible for service or replacement without removal or destruction of luminaire.

Normally retain Constant Voltage driver option. If specifying the BIOS module only retain Constant Current driver option.

LED Drivers: Provide [constant voltage] [constant current] LED drivers that are electronic, UL Class 2, constant-current type and that comply with the following requirements:

The combined driver and LED light source system shall not exceed the minimum luminaire efficacy values as listed in the luminaire schedule provided.

Operates at a voltage of [120-277] [120] 277 volts at 50/60 hertz, with input voltage fluctuations of plus/minus 10 percent.

Dimmable LED drivers should be specified with dimming down to at least 10 percent. Dimmable drivers with a dimming range down to 1 percent should be specified for applications where audio/visual presentations are common such as conference and meetings rooms, hospitality, etc.

Power Factor (PF) greater than or equal to 0.90 at full input power and across specified dimming range.

Maximum Total Harmonic Distortion (THD) less than 20 percent at full input power and across specified dimming range.

Operates for at least 50,000 hours at maximum case temperature and 90 percent non-condensing relative humidity.

Withstands Category A surges of 2 kV without impairment of performance. Provide surge protection that is integral to the driver.

Integral thermal protection that reduces the output power to protect the driver and light source from damage if the case temperature approaches or exceeds the driver's maximum operating temperature.

Complies with the requirements of the Federal Communications Commission (FCC) rules and regulations, Non-Consumer (Class A) for EMI/RFI (conducted and radiated) per 47 CFR 15.

Class A sound rating.

Restriction of Hazardous Substances (RoHS) compliant per EU Directive 2011/65/EU.

Provide dimming capability as indicated in the luminaire schedule on Drawings.[ Dimmable drivers shall dim down to [10] [5] [1] percent. Dimmable drivers shall be controlled by a [Class 2 low voltage 0-10VDC controller] [Digital Addressable Lighting Interface (DALI)] dimming signal protocol, unless otherwise specified. LED drivers of the same family/series shall track evenly across multiple luminaires at all light levels.]

Provide remote LED Drivers that are UL listed for dry locations typical of interior installations. Provide LED driver in junction box or housing with mounting plate. Housing shall allow for field connections to occur inside the housing or shall contain mechanical connections.

LED drivers shall have clear markings indicating dimming type and indicate proper terminals for the various outputs.

SUSPENSION SYSTEM

Ceiling Suspension-System: Manufacturer's standard direct-hung system complying with applicable requirements in ASTM C 635.

Product: USG Donn® Brand AX™ Acoustical Suspension System by USG® Ceilings Plus®.

Main and Cross Tees: Steel double-web construction with 15/16 inch type exposed flange.

Structural Classification: Light Duty.

USG offers numerous colors for main and cross tees. Refer to manufacturer's literature for available colors.

Color: Standard flat white 050.

Attachment Devices: Size for five times design load indicated in ASTM C635, Table 1, Direct Hung unless otherwise indicated.

Wire for Hangers, Braces, and Ties: Provide [one of ]the following:

Retain one or more of the following wire types. If retaining only one, delete option in paragraph above. If retaining more than one, specify or indicate locations where each is used on Drawings.

Zinc-Coated, Carbon-Steel Wire: ASTM A641/A641M, Class 1 zinc coating, soft temper.

Stainless-Steel Wire: ASTM A580/A580M, Type 304, nonmagnetic.

Nickel-Copper-Alloy Wire: ASTM B164, nickel-copper-alloy UNS No. N04400.

ASTM A641, Class 1 zinc coating, soft temper, pre-stretched, with a yield stress load of at least time three design load, but not less than 12 gauge.

If retaining below, indicate sizes here or on Drawings.

[Hanger Rods] [Flat Hangers]: Mild steel, [zinc coated] [ or ] [protected with rust-inhibitive paint].

If retaining below, insert sizes here or indicate on Drawings.

[Angle Hangers]: Angles with legs not less than 7/8 inch wide; formed from minimum 0.04 inch thick, galvanized-steel sheet complying with ASTM A653/A653M, G90 coating designation; with bolted connections and 5/16-inch diameter bolts.

[Edge Moldings]: Manufacturer's standard L-shape moldings matching suspension-system tees[ that comply with seismic design requirements], to conceal ends of tees.

MATERIALS

Aluminum Sheet: ASTM B209, stretcher leveled.

Recycled Content: Up to 85 percent.

Steel Sheet: ASTM A1003, Commercial Grade, [Electrogalvanized] [Hot dipped galvanized] [or equal protective coating].

Electrical components (wiring, connectors, etc.) shall comply with Division 26 Sections.

FABRICATION

Cut integrated ceiling panels to accommodate penetrating fire suppression, mechanical, and electrical items.

EXECUTION

EXAMINATION

Verification of Conditions:

Examine areas and conditions, including structural framing and substrates to which integrated ceiling assemblies attach or abut, with installer present, for compliance with requirements for installation tolerances, clearances, accurate locations of connections to building electrical system, and other conditions affecting performance of the Work.

Verify that layout of hangers will not interfere with other work.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Measure each ceiling area and establish layout of integrated ceiling assemblies to balance border widths at opposite edges of each ceiling. Avoid use of less than half width or length panels at borders, and comply with reflected ceiling plans.

Retain first and second options in paragraph below if fire suppression sprinkler heads or HVAC outlets are required to penetrate into integrated ceiling assemblies. Retain third option below if electrical fixtures other than the integrated luminaires are required.

Coordinate integrated ceiling assembly layout with [fire suppression work, ] [mechanical work, ] [electrical fixtures, ] and other suspended or permanent construction that penetrates the ceiling.

SUSPENSION SYSTEM INSTALLATION

BASIC SEISMIC REQUIREMENTS FOR CEILING Installation: Consult your local code professional for information specific to your region. California projects may be governed by DSA and OSHPD.
IBC CATEGORY A, B 
conform to basic minimums established in ASTM C636.
IBC CATEGORY C 
Install to ASTM E580 Seismic Design Category C.
• Minimum 7/8" wall molding
• Suspension system must not be attached to the wall molding
• Minimum 3/8" clearance on all sides
• Minimum 3/8" overlap of the suspension system on the wall molding
• Ends of main beams and cross tees must be tied together to prevent their spreading (ACM7 Seismic Clip satisfies this requirement)
• Safety wires required on luminaires
IBC CATEGORY D, E, F 
Install to ASTM C636 and ASTM E580
• Minimum 2" wall molding
• Suspension system must be attached to two adjacent walls - opposite walls must have a 3/4"
clearance
• Ends of main beams and cross tees must be tied together to prevent their spreading
• Heavy-duty suspension system
• Ceiling areas over 1,000 SF must have horizontal restraint wire or rigid bracing
• Ceiling areas over 2,500 SF must have seismic separation joints or full height partitions
• Ceilings without rigid bracing must have 2" oversized trim rings for sprinklers and other penetrations
• Changes in ceiling plane must have positive bracing
• Cable trays and electrical conduits must be independently supported and braced
• Suspended ceilings will be subject to special inspection
• Perimeter support wires within 8"

Comply with manufacturer's written installation instructions, approved submittals, ASTM C636[, seismic requirements indicated], CISCA's "Ceiling Systems Handbook", and as specified herein.

Suspend ceiling hangers from building's structural members as follows:

Attach hangers to structural members or to post-installed anchors[ or power-actuated fasteners] that extend through permanent metal forms or floor deck into concrete.

Do not support ceilings directly from permanent metal forms or floor deck.

A note in SDI Publication No. 31, "SDI Specifications and Commentary for Composite Steel Floor Deck," Article 5, that includes the caution: "Improper use of rolled-in hanger tabs could result in the overstressing of such tabs and/or the overloading of the composite deck slab." Suspended-ceiling failures and excessive deck deflection have been attributed to overloaded tabs.

Do not attach hangers to steel deck tabs.

In a significant development, late in 2002, SDI changed its long-held position recommending against suspending loads from roof deck. Commentary in SDI Publication No. 31 for steel roof deck stating that "suspended ceilings, light fixtures, ducts, or other utilities shall not be supported by the steel deck" has been eliminated.

[Do not attach hangers to steel roof deck.]

Install carrying channels or other supplemental support, designed to support imposed loads, for attachment of hanger wires in the following locations:

Where spacing of structural members does not permit installation of hanger wires at spacing required.

Where ductwork, equipment, and other non-structural items within ceiling plenum interfere with hanger spacing.

Suspend main tees from overhead construction or carrying channels with hanger wires spaced 48 inches on center along the length of the main runner. Install hanger wires plumb and straight.

Install cross tees at 48 inch spacing between main tees and level the suspension system.

Bracing wires are required to allow the integrated ceiling assembly to "float" without abutting perimeter walls. Additional bracing wires may be required to comply with seismic requirements.

Retain first option below for installation per ASTM C 636/C 636M requiring three full turns (360 degrees each) within a 3-inch length. Retain second option below if desired. Retain last option below for ceilings in schools and essential service buildings based on requirements issued by the Division of the State Architect in California in DSA IR 25-2.

Brace suspension assembly as required to prevent sway movement. Secure bracing wires to ceiling suspension members and to supports [per specified standards.] [with a minimum of four tight turns.] [per California DSA IR 25-2.] Suspend bracing from building's structural members as required for hangers, without attaching to permanent metal forms, steel deck, or steel deck tabs. Fasten bracing wires into concrete with cast-in-place or postinstalled anchors.

Delete subparagraph below if not required. Indicate hanger and brace locations on Drawings.

Secure [flat, angle, channel, and rod hangers ]to structure, including intermediate framing members, by attaching to inserts, eye screws, or other devices that are secure and appropriate for both structure to which hangers are attached and type of hanger involved. Install hangers in a manner that will not cause them to deteriorate or fail due to age, corrosion, or elevated temperatures.

Install wall moldings at intersection of integrated ceiling assemblies and vertical surfaces. Miter corners where wall moldings intersect or install corner caps.

PANEL INSTALLATION

Hang panels from suspension grid by engaging tension clips into tees.

For Wall-to-Wall Integrated Ceiling Assemblies: Cut panels to leave minimum 3/4 inch clearance from walls.

For Floating Integrated Ceiling Assemblies: Arrange [and cut] panels per reflected ceiling drawings. Install diagonal bracing as required to prevent ceiling sway.

LED DRIVERS

Locate remote LED drivers within the maximum distance allowed to minimize voltage drop. Do not locate remote LED drivers further from the light source than specified by the manufacturer. Locate remote LED drivers in dry, well-ventilated, and accessible location, above accessible ceilings or behind a removable wall or ceiling panel. Mount housing or junction box so that it is rigidly and securely fastened in place. Install LED drivers such that components are not in contact with combustible materials unless listed for such condition. Ground remote LED drivers per NFPA 70.

Provide separate compartments for Class 2 wiring connections and for Class 1 wiring connections. Separation shall be barrier-type within the same box or separate boxes with close connector conduit fittings. Field connections shall be inside housing or junction box or secured by a quick disconnect wire connector.

FIELD QUALITY CONTROL

Retain this article if applicable. ASCE/SEI 7 requires special inspections for suspended ceiling systems in Seismic Design Categories D, E, and F; verify requirements of authorities having jurisdiction.

Retain first option below if Owner engages special inspector. Retain second option if Contractor engages special inspector. If retaining second option, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

Special Inspections: [Owner will engage] [Engage] a qualified special inspector to perform on-site special inspections per the Statement of Special Inspections and as follows:

Special Inspector [will] [shall] perform special inspections for [<insert as required>].

Suspended ceiling system.

Hangers, anchors, and fasteners.

CLEANING

Clean exposed surfaces of integrated ceiling assemblies, including trim, edge moldings, and suspension members. Comply with manufacturer's instructions for cleaning and touch up of minor finish damage.

Replace damaged components.

END OF SECTION 09 58 00

C:\DROPBOX (ABA)\_SPECIFICATIONS PROJECTS\2022\2022.S29 USG GUIDE SPEC\04 SPECS\09 58 00_WSX INTEGRATED CEILING ASSEMBLIES VER 4~~~.DOC